## Sheet1
PV Array Sizing
Specification Variables |  |  |  | PV module variables from DataSheet |  |  |  | Results |  |  |  | Formulae for the variable values
Variable Names | Symbol | Value | Unit | Variable Names | Symbol | Value | Unit | Variable Names | Symbol | Value | Unit | Variable Names | Symbol | Formula
Average Monthly Load | Whload | 6882 | kWh/month | PV model | Model | SunPower SPR-230E-WHT-D |  | Area of required PV panel | Aintrinsic | 351.1588 | m^2 | Average Daily Load | Whdaily | Whload/30
Average Daily Load | Whdaily | 229.4 | kWh/day | Open Circuit Voltage | Voc | 48.2 | V | Number of panels required | N | 215.848 |  | Average Daily Output by PV | Whpv | Whdaily
Average Daily Ouput by PV array | Whpv | 229.4 | kWh/day | Short Circuit Current | Isc | 6.05 | A | Total Area for plant | Aestate | 456.5065 | m^2 | Maximum Power | Pmax | Vmp*Imp
Minimum Incident Energy on location | Hatmin | 4.62 | kWh/m2/day | Maximum Power Voltage | Vmp | 40.5 | V |  |  |  |  | Efficiency PV Module | n | (Vmp*Imp)/(Linsol*A)
|  |  |  | Maximum Power Current | Imp | 5.68 | A |  |  |  |  | Area of required PV panel | Aintrinsic | Whpv/(efficiency*Hatmin)
|  |  |  | Maximum Power | Pmax | 230.04 | W |  |  |  |  | Number of PV panel required | N | Aintrinsic/Areaofindividualpanel
|  |  |  | Length | l | 1.64 | m |  |  |  |  | Total area of plant | Aestate | 1.3*Aintrinsic
|  |  |  | Width | b | 0.992 | m
|  |  |  | Area | A | 1.6269 | m^2
|  |  |  | STC Insoation | L | 1000 | W/m2
|  |  |  | Efficiency | n | 0.1414